## Sheet1
Appendix Q
TRIGGER VALUE CALCULATION FOR ADJACENT TO SURFACE WATER DILUTION ANALYSIS
"An analysis of the effect of the proposed drainfield system on the quality of any adjacent surface water
is required by ARM 17.36.312 and 17.30.715(1c). The increase in the nutrient concentration in the surface water
cannot exceed the trigger value (T.V. of 0.01 mg/L nitrate and 0.001 mg/L phosphorous as set forth in Circular DEQ 7."
DILUTION EQUATION: (QD)(CD) + (QL)(CL) < T.V. = non-significant
QD + QL
Note: Effluent flow rate (QD) must be multiplied by the number of drainfields in the subdivision.
NITRATE CALCULATION:
| 7 |  | Number of drainfields in subdivision
QD = | 26.7 | ft³/d | Effluent flow rate from drainfield in cubic feet per day (commonly 200 gpd or 26.7 ft³/d for a 2 - 5 bedroom home)
CD = | 50 | mg/L | Nitrate concentration in mg/L (50 mg/L nitrate-N for standard drainfield, 24 mg/L for Level 2 wastewater treatment system)
QL = | 12 | ft³/s | Flow rate in ft³/s into (or out of) surface water determined by stream gauge (usually the 14-day, 5-year low flow or 14Q5)
CL = | 0 | mg/L | Nitrate concentration (in mg/L) in surface water; can typically assume zero since increase, not total, is important
| 0.0090117 | mg/L = | final result, must be < 0.01 mg/L to be considered nonsignificant nitrate increase
PHOSPHOROUS CALCULATION:
| 7 |  | Number of drainfields in subdivision
QD = | 26.7 | ft³/d | Effluent flow rate from drainfield in cubic feet per day, (commonly 200 gpd or 26.7 ft³/d for a 2 - 5 bedroom home)
CD = | 10.6 | mg/L | Phosphorous concentration in mg/L (commonly 10.6 mg/L) in effluent
QL = | 200 | ft³/s | Flow rate in ft³/s into (or out of) surface water determined by stream gauge (usually the 14-day, 5-year low flow or 14Q5)
CL = | 0 | mg/L | Phosphorous concentration (in mg/L) in surface water; can typically assume zero since increase, not total, is important
| 0.00011465 | mg/L = | final result, must be < 0.001 mg/L to be considered nonsignificant for phosphorous increase