# MONTANA DEPARTMENT OF ENVIRONMENTAL QUALITY

OPERATING PERMIT TECHNICAL REVIEW DOCUMENT

Air, Energy and Mining Division

1520 E. Sixth Avenue

P.O. Box 200901

Helena, Montana 59620-0901

Colstrip Energy Limited Partnership

1087 West River Street, Suite 200

Boise, Idaho 83702

The following table summarizes the air quality programs testing, monitoring, and reporting requirements applicable to this facility.

| Facility Compliance Requirements | Yes | No | Comments |
| --- | --- | --- | --- |
| Source Tests Required | X |  | Method 3B, 6, 7, 9, 19, and 201A |
| Ambient Monitoring Required | X |  |  |
| COMS Required | X |  |  |
| CEMS Required | X |  |  |
| Schedule of Compliance Required |  | X |  |
| Annual Compliance Certification and Semiannual Reporting Required | X |  | Semiannual and Annual |
| Monthly Reporting Required |  | X |  |
| Quarterly Reporting Required | X |  |  |
| Applicable Air Quality Programs |  |  |  |
| ARM Subchapter 7 Montana Air Quality Permits (MAQP) | X |  | #2035-08 |
| New Source Performance Standards (NSPS) | X |  | 40 CFR 60, Subparts Da, Y, and IIII |
| National Emission Standards for Hazardous Air Pollutants (NESHAPS) |  | X |  |
| Maximum Achievable Control Technology (MACT) | X |  | 40 CFR 63, Subparts ZZZZ and UUUUU |
| Major New Source Review (NSR) | X |  |  |
| Risk Management Plan Required (RMP) |  | X |  |
| Acid Rain Title IV |  | X |  |
| Compliance Assurance Monitoring (CAM) | X |  | OP2035-05 Appendix F and G |
| State Implementation Plan (SIP) | X |  | General Requirements |

Table of Contents

Section I.	 General Information	3

A.	Purpose	3

B.	Facility Location	3

C.	Facility Background Information	3

D.	Current Permit Action	8

E.	Taking and Damaging Analysis	8

F.		Compliance Designation	9

Section ii. Summary of Emission Units	10

A.	Facility Process Description	10

B.	Emission Units and Pollution Control Device Identification	10

C.	Categorically Insignificant Sources/Activities	11

section iii. Explanation of Operating Permit Conditions	12

A.	Emission Limits and Standards	12

B.	Monitoring Requirements	13

C.	Test Methods and Procedures	13

D.	Recordkeeping Requirements	13

E.	Reporting Requirements	13

F.		Public Notice	14

section iv. Non-Applicable Requirements Analysis	15

section v.	  FUTURE PERMIT CONSIDERATIONS	17

A.	MACT Standards	17

B.	NESHAP Standards	17

C.	NSPS Standards	17

D.	Risk Management Plan	17

E.	CAM Applicability	17

F.	PSD and Title V Greenhouse Gas Tailoring Rule	18

# Section I.	 General Information

## A.	Purpose

The technical review document (TRD) discusses decisions made regarding the applicable requirements, monitoring plan, and compliance status of emission units affected by the operating permit proposed for this facility. This document is also intended to provide background information not included in the operating permit and to document issues that may become important during modification or renewals of the operating permit.

The technical review document is intended for reference during review of the permit by the United States Environmental Protection Agency (EPA) and the public. Conclusions in this document are based on information provided in the original application submitted by Colstrip Energy Limited Partnership (CELP) on June 8, 1995, additional information submitted on September 25, 1996, October 30, 1996; a renewal application submitted on January 30, 2004, and information received on April 16, 2008; Montana Air Quality Permit (MAQP) Application #2035-03 submitted on July 25, 1997 and additional information submitted on August 12, 1997, August 26, 1997, November 19, 1997, November 25, 1997, and January 5, 1998; MAQP Application #2035-05 on December 30, 2008, and additional information provided on March 31, 2009; an administrative amendment (AA) request submitted on September 4, 2013; and a renewal application submitted on July 23, 2013. A Title V renewal application was received on June 20, 2019. A deminimis request was also received on December 28, 2018, with a request to update the MAQP. The de minimis request was approved by DEQ but was not incorporated into the MAQP. However, since the deminimis request was approved, the minor changes associated with the request have been incorporated into the Title V permit.

## B.	Facility Location

The facility is located 6 miles north of Colstrip, Montana on Highway 39. The legal location is North ½, Section 32, Township 3 North, Range 41 East, Rosebud County, Montana.

## C.	Facility Background Information

#### Montana Air Quality Permit (MAQP)

The original air quality MAQP #2035 was issued to AEM Corporation for the construction and operation of a coal-fired power generation facility and a coal liquefaction-cogeneration facility from the Montana Department of Health and Environmental Sciences, Air Quality Bureau (precursor to the Department of Environmental Quality (Department)) on September 10, 1985. The application was received on April 26, 1985, and deemed complete on June 25, 1985.

The coal-fired power generation facility was identified as a major stationary source as defined in ARM 16.8.921(22)(a). Therefore, a Prevention of Significant Deterioration (PSD) review was conducted for the permit application.

Coal for the facility comes from the Western Energy mine or other nearby mines. The coal used is called culm, which is a refuse coal whose uses are somewhat limited. AEM planned to utilize 364,000 tons per year (TPY) of refuse coal, 220,752 TPY of PDF (char), 359,400 barrels (Bbl) of oil, 390,000,000 cubic feet per year (ft3/yr) of noncondensible gases, 59,568 TPY of water, and use 11,000 TPY of dolomite lime as supplemental boiler sulfur dioxide (SO2) control to produce 30.65 megawatts (MW) of power.

The first change to the permit was given MAQP #2035-A and was issued on December 22, 1987. This permit was issued to Montana One Partners of LaJolla, California who took over ownership from AEM Corporation. The change requested was to allow the company to construct only the power generation portion of the process and to produce 39 gross megawatts (GMW). The Montana One Partners changed the project description. Montana One Partners planned to utilize 306,600 ton/yr of refuse coal to produce 39 GMW of electrical power. A circulating fluidized bed (CFB) combustion boiler with a heat rating of 485 million British Thermal units per hour (MMBtu) per hour is used in conjunction with a limestone injection for SO2 emission control. Approximately 27,000 tons/yr of limestone is used. Only one steam turbine was planned for the project under this application. A baghouse was installed to control particulate emissions. All other equipment involved with the project (e.g., coal handling, crushing and conveying) remained the same as originally proposed in MAQP #2035. The emissions from the handling and crushing are controlled by a baghouse.

MAQP Alteration #2035-02 issued on April 15, 1994, was requested by CELP who was the current owner of the facility. The name on the permit was changed from Montana One Partners to Colstrip Energy Limited Partners. The ownership transfer occurred on June 10, 1988.

The purpose of the revision was to include limitations in the permit to protect the PSD increment for the 3-hour SO2 standard and the Montana ambient air quality 1-hour standard for nitrogen oxides (NOx). The emission limitations were included in Section II.F. and G. These changes did not alter the annual allowable emissions from the plant or the daily SO2 and NOx limitations. The limitations were added to the rolling 30-day averages required under 40 CFR 60, Subpart Da. Modeling was done to determine the amount of increment consumed as a result of these changes to the emission limitations. These changes resulted in modifications to the reporting requirements and compliance demonstrations.

The emission limitations in Section II.F. were developed based on DEQ’s review of information supplied by CELP. CELP proposed SO2 limits of 450 pounds per hour (PPH) on a 3-hour average and 590 PPH on a 1-hour average and a NOx limit of 500 PPH on a one-hour average. DEQ determined that the appropriate SO2 limits should be 432 PPH on a 3-hour average and 574 PPH on a 1-hour average. These limits were arrived at based on the data submitted by CELP with the elimination of the data for June 12, 1992, because of the concerns about the representativeness of the data. After review of the CEMS data submitted, DEQ and CELP determined the NOx limit should be 328 PPH, which was the number modeled in the original application.

DEQ also made several additional changes to the permit. The CEMS installation, operation, and reporting requirements have been clarified. All references to the coal liquefaction-cogeneration facility were removed since the facility was not constructed.

After the preliminary determination (PD) of MAQP #2035-02 was issued, CELP provided comments on the PD dated February 15, 1994. As a result of these comments, DEQ made a number of changes. The changes were completed as requested by CELP, except that DEQ did not change the continuous emission monitor availability requirement. The continuous emission monitor availability remained at 95%. DEQ also included a condition in the permit which required DEQ to notify CELP when a change is made to the Cooperative Enforcement Agreement between Montana and EPA Region VIII concerning the enforcement guidelines for continuous emission monitors. DEQ did not change the general condition Section IV.H or the wording in Section II.R. For clarity, however, the issuance of MAQP #2035-02 did not authorize any new construction at the facility.

MAQP #2035-03 was issued on March 20, 1998. The permit application proposed the removal of the plant-wide emission limits in Section II.F of MAQP #2035-02 and the establishment of emission limits for point sources at the facility. The permit application did not seek any physical or operational changes to any process equipment at the facility. CELP also proposed removing from the permit the reference in Section II.S to the Hydrometrics letter, eliminating the ambient monitoring required in the permit, and clarifying language in Section II.J regarding sulfur content of waste coal.

CELP presented MAQP Application #2035-03 as a major modification of this major stationary source. A major modification means any physical change in, or change in the method of operations of, a major stationary source. The permit application does not propose any physical or operational changes at the facility; however, MAQP Alteration #2035-03 required a Prevention of Significant Deterioration (PSD) review because the proposed particulate matter 10 micrometers or less (PM10) emission limits should have been addressed in PSD Permit Application #2035. Establishing PM10 emission limits on a point source basis resulted in an allowable emissions increase of 17.94 TPY of PM10. This was a significant emissions increase under PSD. DEQ did not anticipate that actual emissions from the facility will change, since there will be no operational changes occurring.

MAQP #2035-03 established emission limits for point sources at the facility and eliminated the total plant emission limits. Total plant emission limits for SO2, NOx, and CO in Section II.F of MAQP #2035-02 were placed on the CFB boiler only. The CFB boiler is the only significant source of SO2, NOx, and CO at the facility. The opacity limitation was placed in a condition and is applicable to all equipment at the facility. PM10 emission limitations were established on the CFB boiler. PM10 emission limitations were also established for all equipment, transfer points, and storage facilities currently controlled by a baghouse. The PM10 emission limitations in the form of grains per dry standard cubic foot (gr/dscf) for these facilities was based on manufacturer’s data submitted by CELP in the permit application.

Section II.S for MAQP #2035-02 required that CELP handle ash disposed on site in accordance with the provisions specified in the Hydrometrics letter of April 24, 1985. The Hydrometrics letter contained provisions that moisture be added to the ash to prevent blowing and the disposal site be operated in a cut and fill operation. The letter also outlined in detail the soil handling and revegetation operations.

DEQ’s concern with the ash disposal area was that compliance be maintained with applicable requirements during operation of the disposal area and when the disposal area is inactive for any extended period of time. Therefore, MAQP #2035-03 requires that water spray be used when ash is being deposited to control fugitive emissions. The permit also includes a provision requiring mitigative measures, including revegetation for the disposal area during inactive periods. This condition is intended to apply during extended inactive periods or closure.

Attachment 1 in MAQP #2035-02 required CELP to monitor PM10, SO2, and ambient wind speed and direction. The current ambient monitoring site is located on the northwestern edge of the facility. The primary wind directions at the facility are from the southwest, west, and northwest. DEQ believes the ambient monitoring site does not monitor a representative portion of the emissions from the facility. In order for the ambient monitors to be exposed to the average annual emissions from the facility, the monitoring site should be situated downwind of the power plant and ash disposal area. This would require that the monitoring site, in general, be located to the north of the CFB boiler stack and east to northeast of the ash disposal area.

Consequently, DEQ determined that completely eliminating the ambient monitoring network operated by CELP would be inappropriate. DEQ determined that the ambient monitoring site should be moved to the east of the facility at a location to be determined by DEQ. MAQP #2035-03 requires that CELP monitor PM10 but, ambient SO2 monitoring would not be required. DEQ is able to monitor the SO2 emitted from the CFB boiler; if CELP demonstrates compliance with their SO2 emission limits, SO2 ambient standards should not be violated.

Section II.J of MAQP #2035-02 required that the sulfur content of waste coal not exceed 3% as received. DEQ removed this condition from MAQP #2035-03 because DEQ has conditions and limitations which protect NAAQS for SO2. MAQP #2035-03 replaced MAQP #2035-02.

DEQ received written comments on the preliminary determination of MAQP #2035-03 from the Northern Cheyenne Tribe and CELP. As a result of these comments DEQ made several changes requested by CELP. CELP requested that DEQ reword all operations referred to as “coal” to “coal/waste coal.”  DEQ responded that coal is a broad enough term to include all varieties of coal CELP is permitted to use at the facility. However, in a meeting on March 4, 1998, CELP explained they were concerned that it could be construed that CELP’s operations referred to as coal where not permitted to process coal refuse. DEQ stated that the facility is permitted in Section II.A.15 to burn coal refuse. DEQ agreed to state in the permit analysis that the facility is permitted to process coal refuse at the facility. The equipment referred to as coal including the truck dump, hoppers, crushers, conveyors, and storage silos and all associated control equipment are permitted to process coal refuse. The meaning of the terms coal and coal refuse for MAQP #2035-03 are defined in 40 CFR 60, Subpart Da.

On April 15, 2008, DEQ received a request to remove the ambient air quality monitoring requirements from MAQP #2035-03. The permit action removed those requirements as well as updated the permit to reflect current permit format, language, and rule references. MAQP #2035-04 replaced MAQP #2035-03.

On December 30, 2008, DEQ received an application from CELP to modify MAQP #2035-04. This requested modification is to establish a mercury emission limit of 0.9 pounds per trillion British thermal units (lb/TBtu) for the Rosebud Power Plant, pursuant to ARM 17.8.771, and to provide an analysis of potential mercury control options. These control options included, but were not limited to, boiler technology, mercury emission control technology, and any other mercury control practices. On January 30, 2009, DEQ requested additional information to support CELP’s proposed mercury emission control strategy. This information was submitted to DEQ on March 31, 2009 and included additional control technology testing results conducted at the Rosebud Power Plant. Based on mercury sampling conducted at the facility, current mercury emissions were estimated to range from approximately 11.4 lb/TBtu to 20.2 lb/TBtu. Therefore, in order to meet the mercury emission limit specified in ARM 17.8.771, a reduction in mercury emissions of approximately 92% to 96% was estimated to be required for this facility. MAQP #2035-05 established a mercury emission limit and associated operating requirements for the Rosebud Power Plant in order to comply with ARM 17.8.771. MAQP #2035-05 replaced MAQP #2035-04.

On September 4, 2013, DEQ received a de minimis change notice and AA request from Bison Engineering, Inc. (Bison), on behalf of CELP, proposing the inclusion of a 25,000 ton open coal storage pile at the CELP facility.  The storage pile was to serve as a readily accessible stockpile of suitable coal during periods when dry coal was not available from the mine. The permit action incorporated the de minimis coal storage pile and updated language and rule references were applicable. MAQP #2035-06 replaced MAQP #2035-05.

On June 20, 2019, DEQ received a complete application in accordance with the requirements of ARM 17.8.771(9) to address the Best Available Control Technology (BACT) requirement for mercury emissions. ARM 17.8.771(9) requires that no later than 10 years after issuance of a permit containing a mercury emission limit under ARM 17.8.771(1)(b)(i), and every 10 years thereafter, the affected facility must file an application to establish a revised mercury emission limit. DEQ agreed with CELP to retain the current emission limit of 0.9 pounds per trillion British thermal units (lb/TBtu) on a rolling 12-month average basis. MAQP #2035-07 replaced MAQP #2035-06

On May 17, 2022, DEQ received a de minimis notification from CELP. This notification provided for a request to add an outside limestone storage pile of approximately 5,000 tons.

As both MAQP #2035-07 and Title V Operating Permit (#OP2035-04) include baghouse requirements for limestone unloading, CELP requested that MAQP condition II.A.6 be clarified under an administrative amendment to identify the baghouse requirements are for internal limestone handling only. This administrative amendment provide clarification that the existing MAQP condition II.A.6 is for internal handling only and identifies the outside limestone storage pile. MAQP #2035-08 replaced MAQP #2035-07.

Title V Operating Permit

On June 8, 1995, DEQ received an application from CELP for an operating permit. The permit application was assigned Operating Permit #OP2035-00. Operating Permit #OP2035-00 became final and effective on August 1, 1999.

On January 30, 2004, DEQ received an application for the renewal of Title V Permit #2035-00. In addition, on April 15, 2008, DEQ received a request to remove the ambient air quality monitoring requirements from Permit #OP2035-00. Operating Permit #OP2035-01 replaced Operating Permit #OP2035-00.

On December 29, 2009, DEQ issued a significant modification of CELP’s Title V Operating Permit to incorporate the mercury emission requirements which were included into MAQP #2035-05. Operating Permit #OP2035-02 replaced Operating Permit #OP2035-01.

This permit action was a renewal of CELP’s Title V Operating Permit, for which DEQ received an administratively complete application for renewal on July 23, 2013. In addition, the renewal incorporated conditions for multiple NSPS or MACT affected emission units which were previously considered insignificant. Operating Permit #OP2035-03 replaced Operating Permit #OP2035-02.

On June 20, 2019, DEQ received a request for CELP’s Title V renewal. In addition, the renewal incorporated some changes for coal piles which were approved to be incorporated into MAQP #2035-07. Operating Permit #OP2035-04 replaced Operating Permit #OP2035-03

On May 17, 2022, DEQ received a de minimis notification from CELP. This notification provided for a request to add an outside limestone storage pile of approximately 5,000 tons.

As both MAQP #2035-07 and Title V Operating Permit (#OP2035-04) include baghouse requirements for limestone unloading, CELP requested that condition II.D.2 in #OP2035-04be clarified under an administrative amendment to identify the baghouse requirements are for internal limestone handling only. This administrative amendment provide clarification that the existing condition II.D.2 is for internal handling only and identifies the outside limestone storage pile. Operating Permit #OP2035-05 replaces Operating Permit #OP2035-04.

## D.	Current Permit Action

On April 21, 2025, DEQ received an application for renewal of CELP’s Title V operating permit. In addition, DEQ updated language in the permit consistent with current internal processes. Operating Permit #OP2035-06 replaced Operating Permit #OP2035-05.

## E.	Taking and Damaging Analysis

House Bill (HB) 311, the Montana Private Property Assessment Act, requires analysis of every proposed state agency’s administrative rule, policy, permit condition or permit denial, pertaining to an environmental matter, to determine whether the state action constitutes a taking or damaging of private real property that requires compensation under the Montana or U.S. Constitution. As part of issuing an operating permit, DEQ is required to complete a Taking and Damaging Checklist. As required by 2-10-101 through 2-10-105, Montana Code Annotated (MCA), DEQ conducted the following private property taking and damaging assessment.

| YES | NO |  |
| --- | --- | --- |
|  |  | 1. Does the action pertain to land or water management or environmental regulation affecting private real property or water rights? |
|  |  | 2. Does the action result in either a permanent or indefinite physical occupation of private property? |
|  |  | 3. Does the action deny a fundamental attribute of ownership? (ex.: right to exclude others, disposal of property) |
|  |  | 4. Does the action deprive the owner of all economically viable uses of the property? |
|  |  | 5. Does the action require a property owner to dedicate a portion of property or to grant an easement? [If no, go to (6)]. |
|  |  | 5a. Is there a reasonable, specific connection between the government requirement and legitimate state interests? |
|  |  | 5b. Is the government requirement roughly proportional to the impact of the proposed use of the property? |
|  |  | 6. Does the action have a severe impact on the value of the property? (consider economic impact, investment-backed expectations, character of government action) |
|  |  | 7. Does the action damage the property by causing some physical disturbance with respect to the property in excess of that sustained by the public generally? |
|  |  | 7a. Is the impact of government action direct, peculiar, and significant? |
|  |  | 7b. Has government action resulted in the property becoming practically inaccessible, waterlogged or flooded? |
|  |  | 7c. Has government action lowered property values by more than 30% and necessitated the physical taking of adjacent property or property across a public way from the property in question? |
|  |  | Takings or damaging implications? (Taking or damaging implications exist if YES is checked in response to question 1 and also to any one or more of the following questions: 2, 3, 4, 6, 7a, 7b, 7c; or if NO is checked in response to questions 5a or 5b; the shaded areas) |

Based on this analysis, DEQ determined there are no taking or damaging implications associated with this permit action.

## F.	Compliance Designation

DEQ conducted a Full Compliance Evaluation (FCE) on September 11, 2024. The FCE included compliance reports/records submitted by CELP for the review period of July 16, 2022, through September 11, 2024, and an on-site facility inspection conducted on September 11, 2024.

Based on findings at the time of the facility inspection and review of reports and records, DEQ, determined CELP to be in compliance with the terms and conditions of the effective operating permit and reference rules and regulations.

# Section ii. Summary of Emission Units

## A.	Facility Process Description

CELP is an electric generating facility designed to burn low-BTU waste coal from mining operations east of Billings, Montana. The facility uses a CFB boiler. The CFB boiler is designed to efficiently utilize low-Btu coal while also allowing a high recovery of fuel sulfur through the injection of limestone into the fluidized bed.

Coal is delivered to this facility using covered trucks and trailers. Coal storage at the facility is provided through the truck hopper (80 ton capacity), the boiler coal bunkers (1,700 ton capacity), and a single open coal storage pile (25,000 ton). The coal is crushed in primary and a secondary crushers, then conveyed directly to the boiler house coal bunker. The crushed coal is metered to the fluidized bed portion of the boiler using gravimetric feeders.

Limestone is delivered to this facility in trucks and trailers and is unloaded pneumatically into an 820 ton silo. From the silo, limestone is metered to the boiler using gravimetric feeders and a pressure pneumatic conveying system. In the boiler, the coal is burned at relatively low temperatures to minimize NOx formation. Limestone fed to the boiler acts as a reactant for removing SO2.

Ash from the boiler is discharged as either bedash or flyash. Both types of ash are collected in separate systems and conveyed pneumatically to a common ash silo. The combined ash is unloaded periodically into a plant ash truck and transported to an on-site disposal area.

## B.	Emission Units and Pollution Control Device Identification

| Emission Unit ID | Description | Pollution Control Device/Practice |
| --- | --- | --- |
| EU001 | Truck Transport of Coal | Reasonable Precautions and Covered Haul Trucks |
| EU002 | Truck Unloading of Coal | Baghouse |
| EU003 | Coal Crushing and Transport | Baghouse |
| EU004 | Coal Bunker Bin Vents | Baghouses |
| EU005 | Limestone Unloading, Handling, and Storage | Fabric Filter Baghouse and Cartridge Filter |
| EU006 | Circulating Fluidized Bed Boiler | Baghouse |
| EU007 | Flyash Conveying and Storage | Baghouse |
| EU008 | Bedash Conveying and Storage | Baghouse |
| EU009 | Ash Storage Silo Unloading | Baghouse |
| EU010 | Ash Truck Unloading | Water Spray |
| EU011 | Fugitive Emissions: Ash Disposal Area | Water Spray |
| EU012 | Fugitive Emissions: Vehicle Traffic | Paving or chemical dust suppression or water spray as backup |
| EU013 | Open Coal Storage Piles (Two) | Reasonable Precautions (chemical suppression) |
| EU014 | Diesel-Fired Emergency Boiler Feed Pump | Engine Design |
| EU015 | Diesel-Fired Fire Water Supply Pump | Engine Design |
| EU016 | Diesel-Fired Portable Welder | Engine Design |

## C.	Categorically Insignificant Sources/Activities

The following table lists the significant emission units located at the CELP facility.

| Emission Unit ID | Description |
| --- | --- |
| IEU01 | Fugitive Emissions: Diesel Fuel Combustion |
| IEU02 | Diesel Fuel Oil Storage Tanks |
| IEU05 | Propane-fired Portable Heaters |

# section iii. Explanation of Operating Permit Conditions

## A.	Emission Limits and Standards

Applicable requirements for significant emission units are listed after each emission unit. At the time of permit issuance, the requirements listed underneath each emission unit or group of emission units are believed to be the applicable requirements. DEQ does not intend for the facility-wide conditions to supersede the applicable requirements listed below each emission unit or group of emission units.

Section II.A.20 of MAQP #2035-07 states that opacity shall not exceed 20% or greater averaged over 6 consecutive minutes. The rule citation for Section II.A.11 is ARM 17.8.304. ARM 17.8.304(4) states that this rule does not apply to those new stationary sources listed in ARM 17.8.340 for which a visible emission standard has been promulgated. Subpart Da - Standards of Performance for Electric Utility Steam Generating Units for Which Construction Is Commenced After September 18, 1978 is an applicable requirement for the CFB boiler. Therefore, the opacity limit on the CFB boiler in Operating Permit #OP2035-00 is 40 CFR 60.42Da(b). 40 CFR 60.42Da(b) states that a facility shall not cause to be discharged into the atmosphere from any affected facility any gases which exhibit greater than 20 percent opacity (6 minute average) except for one 6 minute period per hour of not more than 27 percent opacity (ARM 17.8.340 and 40 CFR 60.42Da(b)).

The NOx emission limitations and monitoring requirements contained in Subpart Da do not apply to CELP since the facility burns more than 25%, by weight, refuse coal (40 CFR 60.44Da(a)(1)). However, CELP is subject to annual, daily, and hourly NOx emission limits established to protect ambient air quality. Section III.E.2. of the operating permit contains the applicable NOx limits.

Demonstration of compliance to the SO2 limitations contained within 40 CFR Subpart 60. 43(a)(1) shall follow the requirements of 40 CFR Subpart Da 49 and 50, including Reference Method 19 of Appendix A (40 CFR Part 60) and using a single F-Factor of 10,024 dscf/MMBtu. The establishment of the single F-Factor was initiated as a result of comments to the issuance of the Draft Title V #OP2035-01. Subsequent to discussion with DEQ the concluding F-Factor value and justification was presented by Bison, on behalf of CELP, in a correspondence dated October 13, 2008. DEQ formally agreed with the 10,024 dscf/MMBtu value through issuance of the Proposed Renewal Operating Permit on October 29, 2008.

40 CFR 60, Subpart Y - Standards of Performance for Coal Preparation Plants is applicable to emission units Truck Unloading of Coal (EU002), Coal Crushing and Transport (EU003), Coal Bunker Bin Vents (EU004), and the Open Coal Storage Piles (EU013).

CELP is not an affect unit subject to the Acid Rain Program as the plant meets the definition of a qualifying facility under 40 CFR 72.2 and the applicability criterion listed under 40 CFR 72.6(b)(5).

## B.	Monitoring Requirements

ARM 17.8.1212(1) requires that all monitoring and analysis procedures or test methods required under applicable requirements are contained in operating permits. In addition, when the applicable requirement does not require periodic testing or monitoring, periodic monitoring must be prescribed that is sufficient to yield reliable data from the relevant time period that is representative of the source’s compliance with the permit.

The requirements for testing, monitoring, recordkeeping, reporting, and compliance certification sufficient to assure compliance does not require the permit to impose the same level of rigor for all emission units. Furthermore, it does not require extensive testing or monitoring to assure compliance with the applicable requirements for emission units that do not have significant potential to violate emission limitations or other requirements under normal operating conditions. When compliance with the underlying applicable requirement for an insignificant emissions unit is not threatened by lack of regular monitoring and when periodic testing or monitoring is not otherwise required by the applicable requirement, the status quo (i.e., no monitoring) will meet the requirements of ARM 17.8.1212(1). Therefore, the permit does not include monitoring for insignificant emission units.

This permit includes periodic monitoring or recordkeeping for each applicable requirement. The information obtained from the monitoring and recordkeeping will be used by CELP to periodically certify compliance with the emission limits and standards. However, DEQ may request additional testing to determine compliance with the emission limits and standards.

ARM 17.8.771, Mercury Emission Standards for Mercury-Emitting Generating Units, applies to the CELP. This rule requires mercury monitoring be conducted by CELP. Mercury monitoring provisions are contained in the Title V operating permit and outlined in Appendix H of Operating Permit #OP2035-02.

## C.	Test Methods and Procedures

The operating permit may not require testing for all sources if routine monitoring is used to determine compliance, but DEQ has the authority to require testing if deemed necessary to determine compliance with an emission limit or standard. In addition, CELP may elect to voluntarily conduct compliance testing to confirm its compliance status.

## D.	Recordkeeping Requirements

CELP is required to keep all records listed in the operating permit as a permanent business record for at least 5 years following the date of the generation of the record.

## E.	Reporting Requirements

Reporting requirements are included in the permit for each emissions unit and Section V of the operating permit “General Conditions “explains the reporting requirements. However, CELP is required to submit semi-annual and annual monitoring reports to DEQ and to annually certify compliance with the applicable requirements contained in the permit. The reports must include a list of all emission limit and monitoring deviations, the reason for any deviation, and the corrective action taken as a result of any deviation.

## F.	Public Notice

In accordance with ARM 17.8.1232, a public notice was published in the Forsyth Independent Press newspaper on or before May 28, 2026.  DEQ provided a public comment period on the draft operating permit from May 28, 2026, to June 29, 2026.  ARM 17.8.1232 requires DEQ to keep a record of both comments and issues raised during the public participation process.  The comments and issues received by June 29, 2026, will be summarized, along with DEQ's responses, in the following table.  All comments received during the public comment period will be promptly forwarded to CELP so they may have an opportunity to respond to these comments as well.

# section iv. Non-Applicable Requirements Analysis

Pursuant to ARM 17.8.1221, CELP requested a permit shield for all non-applicable regulatory requirements and regulatory orders identified in the tables in Section 8 of the permit application. In addition, the CELP permit application identified a permit shield request for applicable requirements for both the facility and for certain emission units. DEQ has determined that the requirements identified in the permit application for the individual emissions units are non-applicable. These requirements are contained in the permit in Section IV- Non-applicable Requirements.

The following table outlines those requirements that CELP had identified as non-applicable in the permit application but will not be included in the operating permit as non-applicable. The table includes both the applicable requirement and reason that DEQ did not identify this requirement as non-applicable.

Table 3. Regulations Not Identified as Non-Applicable By DEQ. Table 3 lists the requirements that DEQ did not agree were non-applicable.

| Reason | Rule Citation |  |
| --- | --- | --- |
| These rules do not have specific requirements for major sources because they are requirements for EPA or state and local authorities. These rules can be used as authority to impose specific requirements on a major source. | 40 CFR 51 40 CFR 71 |  |
| These regulations may not be applicable to the source at this time, however, these regulations may become applicable during the life of the permit. | ARM 17.8.514 ARM 17.8.515 ARM 17.8.611 ARM 17.8.612 ARM 17.8.740 et seq. ARM 17.8.818-828 | 40 CFR 60.14 40 CFR 60.15 |
| This federal regulation has specific procedural requirements that may become relevant during the permit term. | 40 CFR 61 Subpart M |  |
| This rule contains requirements for regulatory authorities and not major sources; this rule can be used to impose specific requirements on a major facility. | 40 CFR 62 |  |
| These regulations are applicable requirements to specific emissions units; therefore, a facility wide shield will not be granted. | ARM 17.8.340 |  |
| These rules include either a statement of purpose, applicability statement, regulatory definitions, or a statement of incorporation by reference. Therefore, facility wide permit shields will not be granted for these rules. | ARM 17.8.301 ARM 17.8.302 ARM 17.8.341 ARM 17.8.342 ARM 17.8.601 ARM 17.8.901 et. seq. ARM 17.8.1001 et. seq. ARM 17.8.1100 et. seq. | 40 CFR 52 40 CFR 63 Subpart A 40 CFR 63 Subpart B |
| Repealed Regulations | ARM 16.8.1414 ARM 16.8.1419 |  |
| This rule may or may not be relevant but DEQ will not be granting a shield for this rule. | 40 CFR 70 |  |

# section v.	  FUTURE PERMIT CONSIDERATIONS

## MACT Standards

On February 16, 2012, EPA finalized the Mercury Air Toxics Standard (MATS) rule, also known as the Utility MACT, which was promulgated under 40 CFR 63, Subpart UUUUU – National Emission Standards for Hazardous Air Pollutants: Coal and Oil-Fired Electric Utility Steam Generating Units. The CELP facility is an affected source pursuant to this MACT standard, which had a compliance date of April 16, 2015.

As of the issuance of this action, DEQ is not aware of any future MACT standards to be promulgated that may affect the facility.

## NESHAP Standards

As of the issuance date, DEQ is unaware of any future requirement that may be promulgated during the permit term for which this facility must comply other than 40 CFR 61, Subpart M for Asbestos.

## NSPS Standards

As of the issuance date, DEQ is unaware of any NSPS Standards that are applicable to the facility other than 40 CFR 60, Subpart Da for the CFB Boiler and 40 CFR 60, Subpart Y for coal handling.

## Risk Management Plan

As of the issuance date, this facility does not exceed the minimum threshold quantities for any regulated substance listed in 40 CFR 68.115 for any facility process. Consequently, this facility is not required to submit a Risk Management Plan.

If a facility has more than a threshold quantity of a regulated substance in a process, the facility must comply with 40 CFR 68 requirements within 3 years after the date on which a regulated substance is first listed under 40 CFR 68.130; or the date on which a regulated substance is first present in more than a threshold quantity in a process, whichever is later.

## CAM Applicability

An emitting unit located at a Title V facility that meets the following criteria listed in ARM 17.8.1503 is subject to Subchapter 15 and must develop a CAM Plan for that unit:

- The emitting unit is subject to an emission limitation or standard for the applicable regulated air pollutant (other than emission limits or standards proposed after November 15, 1990, since these regulations contain specific monitoring requirements,

- The emitting unit uses a control device to achieve compliance with such limit; and

- The emitting unit has potential pre-control device emissions of the applicable regulated air pollutant that is greater than major source thresholds.

CELP meets the above criteria for particulate matter (PM) and SO2. Refer to Appendix F and Appendix G of Operating Permit #OP2035-02 for a summary of the CAM plans.

## PSD and Title V Greenhouse Gas Tailoring Rule

On May 7, 2010, EPA published the “light duty vehicle rule” (Docket # EPA-HQ-OAR- 2009-0472, 75 FR 25324) controlling greenhouse gas (GHG) emissions from mobile sources, whereby GHG became a pollutant subject to regulation under the Federal and Montana Clean Air Act(s). On June 3, 2010, EPA promulgated the GHG “Tailoring Rule” (Docket # EPA-HQ-OAR-2009-0517, 75 FR 31514) which modified 40 CFR Parts 51, 52, 70, and 71 to specify which facilities are subject to GHG permitting requirements and when such facilities become subject to regulation for GHG under the PSD and Title V programs.

Under the Tailoring Rule, any PSD action (either a new major stationary source or a major modification at a major stationary source) taken for a pollutant or pollutants other than GHG that would become final on or after January 2, 2011 would be subject to PSD permitting requirements for GHG if the GHG increases associated with that action were at or above 75,000 TPY of carbon dioxide equivalent (CO2e) and greater than 0 TPY on a mass basis. Similarly, if such action were taken, any resulting requirements would be subject to inclusion in the Title V Operating Permit. Facilities which hold Title V permits due to criteria pollutant emissions over 100 TPY would need to incorporate any GHG applicable requirements into their operating permits for any Title V action that would have a final decision occurring on or after January 2, 2011.

Starting on July 1, 2011, PSD permitting requirements would be triggered for modifications that were determined to be major under PSD based on GHG emissions alone, even if no other pollutant triggered a major modification. In addition, sources that are not considered PSD major sources based on criteria pollutant emissions would become subject to PSD review if their facility-wide potential emissions equaled or exceeded 100,000 TPY of CO2e and 100 or 250 TPY of GHG on a mass basis depending on their listed status in ARM 17.8.801(22) and they undertook a permitting action with increases of 75,000 TPY or more of CO2e and greater than 0 TPY of GHG on a mass basis. With respect to Title V, sources not currently holding a Title V permit that have potential facility-wide emissions equal to or exceeding 100,000 TPY of CO2e and 100 TPY of GHG on a mass basis would be required to obtain a Title V Operating Permit.

Based on information provided by CELP, CELP’s potential emissions exceed the GHG major source threshold of 100,000 TPY of CO2e for both Title V and PSD under the Tailoring Rule.

The Supreme Court of the United States (SCOTUS), in its Utility Air Regulatory Group v. EPA decision on June 23, 2014, ruled that the Clean Air Act neither compels nor permits EPA to require a source to obtain a PSD or Title V permit on the sole basis of its potential emissions of GHG. SCOTUS also ruled that EPA lacked the authority to tailor the Clean Air Act’s unambiguous numerical thresholds of 100 or 250 TPY to accommodate a CO2e threshold of 100,000 TPY. SCOTUS upheld that EPA reasonably interpreted the Clean Air Act to require sources that would need PSD permits based on their emission of conventional pollutants to comply with BACT for GHG. As such, the Tailoring Rule has been rendered invalid and sources cannot become subject to PSD or Title V regulations based on GHG emissions alone. Sources that must undergo PSD permitting due to pollutant emissions other than PSD may still be required to comply with BACT for GHG emissions.