## Slide 1
Copyright © Baringa Partners LLP 2025. All rights reserved.
This document is subject to contract and contains confidential and proprietary information.
Energy & Resources | US Utilities
6/23/2024
GRACI Project Overview
Montana Resilience Workshop

## Slide 2: Table of contents
2 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential
1 | Purpose & Background
2 | Grid Resilience Report (GRR)
3 | State of the Grid Report (SOGR)
4 | Group Q&A
5 | Appendix

## Slide 3: 1. Purpose & Background
3 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential

## Slide 4: This presentation will review the main takeaways from the GRACI technical assistance program in preparation for 40101(d) funding and improving MT grid resilience more broadly
4 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential
PURPOSE & BACKGROUND | GRACI OVERVIEW
GRID RESILIENCE REPORT (GRR)
Deliverable Purpose
Identify the counties in Montana with the highest future risk for extreme weather-related impacts
Highlight ways in which utilities can invest to prepare for changes in future risk profile
STATE OF THE GRID REPORT (SOGR)
Deliverable Purpose
Identify the most historically impactful extreme weather events to Montana customers between 2018 - 2022
Highlight the counties in Montana that historically have seen the most severe outages from
extreme weather

## Slide 5: 2. Montana Grid Resilience Report (GRR)
5 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential
Key Findings

## Slide 6: Baringa is leveraging forward-looking climate projections to inform its technical assistance work for states in WECC
GRID RESILIENCE REPORTS | DATA SOURCES
Source: Western Regional Climate Center (WRCC) Input metric: Hourly max wind speed (mph)
Output: Wind speed at key return periods via GEV distribution
Wind
Flood
Source: Hydrosource (ORNL) Input metric: Annual Variable Infiltration Capacity (VIC) model runoff (mm/year)
Output: Average annual VIC runoff (pluvial flooding) for 4 warming scenarios and 3 time periods (historical, mid-century, end-century)
Precipitation
Source: CLIMRR (ANL)
Input metric: Annual total precipitation (in/year) by grid cell Output: Max annual total precipitation (in/year) by county
Drought
Source: CLIMRR (ANL)
Input metric: Consecutive days with no precipitation by grid cell Output: Max consecutive days with no precipitation by county
Heat
Source: CLIMRR (ANL)
Input metrics:
Days above 95, 105, 115, 125 °F
Annual cooling degree days
Seasonal maximum temperatures
Output: Input metrics applied from a grid cell level to a county level
Cold
Source: CLIMRR (ANL)
Input metrics:
Annual minimum temperature
Annual heating degree days
Seasonal minimum temperatures
Output: Input metrics applied from a grid cell level to a county level
Wildfire
Source: CLIMRR (ANL)
Input metric: Fire weather index (FWI) by grid cell
Output: Maximum fire weather index by county

## Slide 7: This report is standardized to include 3 different data visualizations that provide insights for Distribution and Transmission across 7 extreme weather hazards
GRID RESILIENCE REPORTS | ANALYSIS APPROACH
1
Distribution Maps
Purpose: Uses population as proxy for volume of distribution assets given that the location of distribution assets is restricted.
Interpretation*: Locate areas of high exposure by identifying counties with coincident large bubbles and dark colors. This indicates a combination of high volume of Dx assets and significantly high extreme weather projections.
2
Transmission Maps
Purpose: Overlays transmission assets on climate projections by county.
Interpretation: Locate areas of high exposure by identifying assets in counties of high risk. Exposure differs by asset class and will be highlighted in Key Insights tables throughout.
*Note: Analysis addresses risk given volume of assets and does not account for risk to remote customers at end of radial distribution grids.

## Slide 8: Utilities could consider additional fire mitigation initiatives in western counties which face increasing fire risk over time and have high Dx asset densities
WILDFIRE | SPATIAL ANALYSIS
KEY OBSERVATIONS
Historical wildfire exposure is concentrated in Montana’s eastern counties.
High percentage of undergrounding, pole upgrades, and covered conductor 40101(d) proposals indicate general alignment with wildfire exposure, but utilities could consider vegetation management projects as well.
Gallatin and Cascade Counties both border high exposure counties,
putting a high density of Dx assets at risk in the case of fire spread.
Montana Summer Fire Weather Index (FWI)
Distribution Assets (Population), Historical
Montana Summer Fire Weather Index (FWI)
Distribution Assets (Population), End-Century [RCP-8.5]
FWI increases tend to be more pronounced in western counties, contributing to a convergence of state-wide fire exposure.
Despite the lower population density of Montana’s eastern counties, stretches of Dx assets in the region are highly exposed.
Low High
Historical, Population
End-Century, Population
+25%
Yellowstone County
KEY OBSERVATIONS
FWI increases by about 2-5 points across the state, demonstrating the importance of utilizing forward-looking climate projections for state- wide fire mitigation planning.
Large population center (high density of Dx and
Tx assets) highly exposed to wildfire, marking a potential priority area for investment.
Low High
+13%
Billings
Helena
Helena
Billings
Population1
50k
30k
5k
Population1
50k
30k
5k
KEY HV Tx EXPOSURE CORRIDOR
Colstrip Lines
North Plains Connector

## Slide 9: By mid-century, fire exposure decreases between summer and autumn, while by end-century it is expected to increase in severity and duration, shortening the maintenance window
WILDFIRE | STATISTICAL ANALYSIS
Montana Average Seasonal Fire Weather Index (FWI)
Population-Weighted by County [RCP-8.5]
Key Highlights | Analysis
Elevated Exposure by End-Century | End-century wildfire exposure is elevated, with the sharpest increase occurring between spring and autumn by about 20% from historical FWI.
Lengthened Fire Season | Elevated wildfire exposure around the summer suggests a lengthening of the wildfire season combined with an increase in severity. This lengthening is most pronounced between summer and autumn by mid- century, and between spring and summer by end-century.
Shortened Maintenance Window | The change in length of wildfire seasons suggest that the window for scheduled maintenance during the shoulder seasons is diminishing.
0
28
26
24
22
20
18
16
14
12
10
8
6
4
2
Fire Weather Index
Winter
Spring
Summer
Autumn
+20%
Historical Mid-Century End-Century

## Slide 10: Utilities could consider planning beyond required wind design standards and invest in vegetation management and undergrounding projects in south-central counties
WIND | SPATIAL ANALYSIS
Montana 100-year Wind Speed (mph)
Historical
45 mph 150 mph
Historical, Population
Key Highlights | Analysis
Distribution | Rather than targeted investments, wind exposure could be addressed through upgraded design standards across a utility service territory
Yellowstone County | Yellowstone County has a population of approximately 170k and 100-year return value of 98 mph, indicating a high exposure area for Dx assets
South- Central Counties | South-central counties generally exhibit high wind gust speeds, posing a threat to Dx assets in this region which also have high wildfire exposure Undergrounding, pole upgrades, and vegetation management address both of these hazards simultaneously
Vegetation management projects in north-central counties could simultaneously address high levels of exposure to wind and wildfire.
98
mph
119
mph
Population1
50k
30k
5k
150
mph
86
mph

## Slide 11: Utilities could consider reinforcing Tx structures for MV/HV lines in NW and SW counties and continue undergrounding and vegetation management projections to address wind exposure
WIND | SPATIAL ANALYSIS
Montana 100-year Wind Speed (mph)
Historical
Key Highlights | Analysis
Transmission | Yellow Stone County: Multiple MV-HV transmission lines intersect in Yellowstone and Park Counties, where they are exposed to high wind return values. Glacier County: LV/MV lines in Glacier County are exposed to peak state wind levels. Vegetation Management: While transmission lines typically have greater clearance than distribution infrastructure, utilities could consider expanding vegetation management efforts or standardizing cycles to reduce risk to assets. North Plains Connector: Proposed North Plains Connector has low exposure.
Transmission Infrastructure
50 mph 130 mph
Utilities could prioritize hardening for portions of
Tx lines that pass through high exposure counties.
100-161kV
220-287kV
345kV
Billings
Helena
<100kV
North Plains Connector Proposed Route
Transmission Voltage Key
500kV

## Slide 12: Increases in extreme heat exposure suggest that utilities could prioritize substation and Dx line upgrades in eastern counties to address derating, degradation, and potential failure
EXTREME HEAT | SPATIAL ANALYSIS
KEY OBSERVATIONS
Currently, Tx and Dx assets have no exposure to days above 105 °F.
105 °F is an important threshold for distribution assets and substations, which
can fail when exposed to two consecutive days above 104°F.2
Round 1 projects generally addressed extreme heat through undergrounding, line upgrades, and substation upgrades.
KEY OBSERVATIONS
Eastern counties are expected to face about 5-7 days >105 °F annually by mid- century, contributing to high Dx asset utilization/degradation, derating, capacity violations, and potential failure.
Montana Days Above 105 °F
Distribution Assets (Population), Historical
Montana Days Above 105 °F
Distribution Assets (Population), End-Century [RCP-8.5]
On average, no counties historically experience any days above 105 °F in a given year.
0 Days 10 Days
End-Century, Population
Historical, Population
0 Days 10 Days
Yellowstone County
1Population bubbles are continuous and therefore labels are approximate. 2EPRI Climate READi
6 days
4 days of >104 °F exposure could justify substation and Dx line upgrades to mitigate potential failure and avoid derating for a high density of Dx assets.
Billings
Helena
Helena
Population1
50k
30k
5k
Population1
50k
30k
5k
Extreme heat typically manifests most directly in issues for substations and transformers.
4 days
Billings
220kV+ transmission lines are exposed to high
levels of extreme heat in southern counties, which can cause capacity derates and line sag.

## Slide 13: Utilities could continue to fund distribution asset weatherization such as undergrounding and pole upgrades to address cold exposure
EXTREME COLD | SPATIAL ANALYSIS
KEY OBSERVATIONS
Extreme cold coincides with large population centers in the western portion of the state, indicating high levels of Dx asset exposure.
Prevalence of proposals including undergrounding and pole upgrades seems to address extreme cold exposure, but MDEQ could consider Dx asset density in its project awards going forwards.
Montana Average Annual Minimum Temperature (°F)
Distribution Assets, (Population) Historical
Montana Average Annual Minimum Temperature (°F)
Distribution Assets, (Population), End-Century [RCP-8.5]
17°F 55°F
17°F 55°F
End-Century, Population
Annual minimum temperatures rise about 10°F by end-century but remain near freezing across many western counties.
Flathead
County
KEY OBSERVATIONS
Climate projections cannot predict acute extreme events like polar vortices and winter storms, underrepresenting cold exposure.
Flathead County is exposed to average annual
minimum temperatures of about 32 °F, indicting continued icing and freezing exposure for Dx assets.
Key Dx exposure corridor
+11 °F
Helena | 
 | +10 °F
Historical, Population
21°F
Billings
Helen
a
Billings
Population1
50k
30k
5k
Population1
50k
30k
5k

## Slide 14: 3. State of the Grid Report (SOGR)
14 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential
Key Findings

## Slide 15: Severe outages were mapped to corresponding weather events to better understand which forms of extreme weather are driving customer interruptions and how utilities can respond
WECC OVERVIEW | APPROACH
DEFINE EXTREME WEATHER EVENTS
FILTER EXTREME OUTAGE EVENTS
ANALYZE EVENT COINCIDENCE
DETERMINE ASSET PLANNING INSIGHTS
Purpose: Begin with a definition of extreme weather to focus on the most impactful events.
Definition: weather events are considered extreme if they are above the 90th percentile of severity for that state.
Data: Western Regional Climate Center (WRCC)
Time: 2018 - 2022
Definition: outage events are considered extreme if:
At least 50% OR >30,000 of customers are out in a single county
*modified from Oak Ridge National Labs definition
Data: EAGLE-I
Time: 2018 - 2022
Purpose: Define extreme outage events to highlight highest cost outages
Purpose: Identify the extreme outages that occur at the same time as extreme weather events.
Analysis Areas:
WECC Overview
Most Impactful Hazard Analysis
Hazard by Total Interruptions (Pareto Chart)
Spatial Analysis
Historical Ignition Analysis
Hazard Deep Dives
Purpose: Provide implications for asset planning and funding priorities
Example Insights
Historical severe outage locations
Historical extreme ignitions
Historical primary drivers of outages
Distribution of outages across hazards
Design standard implications
KEY WEATHER EVENTS
WILDFIRE
SUMMER STORMS
EXTREME PRECIPITATION
WINDSTORM
RAINSTORM
EXTREME HEAT
FLOOD
EXTREME COLD
WINTER STORMS

## Slide 16: Weather events were mapped to raw data to capture both single hazard and multi-hazard events. Events are considered extreme if the raw data is above the 90th percentile for the state
WECC OVERVIEW | WEATHER EVENT MAPPING
*Outages occurring within two days of a documented wildfire ignition in the county of origin were also attributed to wildfire, overriding other hazard combinations
WEATHER EVENT | PRESENT WEATHER METRICS (Above 90th percentile)
EXTREME COLD | Min Temperature
EXTREME HEAT | Max Temperature
WILDFIRE* | Fire Weather Index (FWI)
EXTREME PRECIPITATION | Precipitation
WEATHER EVENT | PRESENT WEATHER METRICS (Above 90th percentile)
WIND STORM | Wind
RAIN STORM | Wind + Precipitation
SUMMER STORM | Wind + Precipitation + Max Temperature
WINTER STORM | Wind + Precipitation + Min Temperature
FLOODING | Surface Runoff

## Slide 17: The EAGLE-I dataset provides coverage for 80% of MT customers, but is missing data from smaller cooperatives in the eastern portion of the state
WECC OVERVIEW | EAGLE-I COVERAGE
EAGLE-I CUSTOMER COVERAGE (%) (MT, 2018-2022)
INSIGHTS
Data fidelity: Outage data generally has better fidelity in the western region of the state than the eastern region
Customer coverage: A high volume of customers (about 80%) in the state are covered by the EAGLE-I dataset, indicating that it is still valuable for volumetric analysis
Weather event coverage: The weather events driving outages in counties
without data will be underrepresented in this analysis (wildfire and extreme heat)
  While this may not have a large impact on the distribution of the volume of customer interruptions, it could significantly change the distribution of the count of outages associate with different hazards
COVERAGE BUCKET
Fergus Electric Cooperative
Marias River Electric Cooperative
Sheridan Electric
Cooperative
Tongue River Electric Cooperative
McCone Electric
Cooperative

## Slide 18
High winds drive the most frequent and impactful power outages in the state, accounting for nearly 60% of all customer interruptions from severe outages across a 5-year period
MONTANA | STATE OVERVIEW
*A severe outage is defined as one in which >50% of customers in a county are out simultaneously, or at least 30,0000 customers in a county experience an outage simultaneously, whichever is less Source: EAGLE-I, WRCC
**Future outlook for the hazard severity based on Baringa’s Grid Resilience Report, completed as part of phase 2 of this analysis (Insert link to the GRR here)
0
10,000 20,000 30,000 40,000 50,000 60,000 70,000
Absolute Outage Severity
(Total Customer Interruptions Coincident with 90th Percentile Weather)
80,000
0.60
0.00
0.65
0.70
0.75
0.80
0.85
0.90
0.95
1.00
1.05
1.10
-0.05
Extreme
Humidity
Extreme Precipitation
Flooding
Extreme Heat Extreme Cold
Rainstorm
Summer Storm
Wildfire
Windstorm
Winter Storm
No Extreme Hazard
SEVERITY & FREQUENCY OF EXTREME OUTAGES*
DURING EXTREME WEATHER
(MT, 2018-2022)
Relative Outage Severity (Median Outage Ratio)
HAZARD INSIGHTS
High winds frequently drive severe outages on the Montana grid
Wind-driven outages account for nearly 60% of all customer interruptions from severe outages across the state from 2018- 2022
Exposure to extreme winter and summer storms is projected to intensify
The MT GRR projects increasing annual precipitation levels, but also prolonged periods of drought across the state in future years, indicating more frequent and severe extreme precipitation events such as winter/summer storms
Extreme wildfire is relatively frequent but accounts for few interruptions
Wildfire is the third most common event (16), but accounts for fewer customer interruptions given its concentration in less populated counties
Outage Count
25
.1110
2
Legend: Most Impactful Hazard Tertiary Hazard No Extreme Hazard

## Slide 19: The majority of customer interruptions from severe outages are concentrated among a few key weather events, including windstorms, summer storms, and winter storms
MONTANA | TOTAL CUSTOMER INTERRUPTIONS
*A severe outage is defined as one in which >50% of customers in a county are out simultaneously, or at least 30,0000 customers in a county experience an outage simultaneously, whichever is less
65,602
44,681
27,335
25,879
23,299
19,534
16,442
8,104
7,142
1,215
70,000
65,000
60,000
55,000
50,000
45,000
40,000
35,000
30,000
25,000
20,000
15,000
10,000
5,000
0
0
10
20
30
40
50
60
70
80
90
100
WindstormSummer Winter Extreme Extreme Storm Storm Precipitation Cold
Extreme Heat
Wildfire Rainstorm
No Extreme Hazard
Flood
Extreme Humidity
32,478
Cumulative % Outage Frequency
Weather Event Type
OUTAGE INSIGHTS
A handful of hazards drive the majority of severe customer interruptions across the state
The top 3 events (windstorms, summer storms, and winter storms) account for about 54% of all customer interruptions resulting from severe outages
Extreme weather drives a high percentage of severe
outages in the state
About 2% of customer interruptions from severe outages were not coincident with at least one extreme weather variable, a much lower percentage than other states in WECC
Utilities could consider which events impact their climate zone
Asset-level vulnerability studies can help prioritize resilience investments by quantifying risk in dollars
Total Customers Interruptions
Cumulative (%)
SEVERE OUTAGES* BY WEATHER EVENT & TOTAL CUSTOMER INTERRUPTIONS
(MT, 2018-2022)

## Slide 20: Wind and flood drive an outsized number of customer interruptions in NW counties, accounting for population, while S counties experience fewer interruptions than expected
MONTANA | HAZARD MAP
PRIMARY DRIVER OF CUSTOMER INTERRUPTIONS BY COUNTY (MT, 2018-2022)
INSIGHTS
The highest volume of customer interruptions is concentrated in western counties with dense vegetation and higher exposure than other regions
While undergrounding projects would address wind exposure in the region, utilities must consider the tradeoffs given high precipitation and flood exposure
Extreme wildfire drives a high volume of customer interruptions in the southeastern portion of the state
Substantiates GRR finding that eastern counties are exposed to peak wildfire risk in the state, which is projected to intensify out to mid- and end-century
A pocket of flood, cold, and wind exposure in the NW portion of the state is driving severe outages
Prevalence of waterways in Lincoln, Sanders, and Flathead counties
contributes to peak state flood exposure
This flood exposure, combined with cold and wind risk in the NW contributes to an outsized number of customer interruptions with respect to population
Total Customer Interruptions
500k
150k
25k
PRIMARY DRIVER

## Slide 21: Counties with the highest volume of interruptions per customer are spread throughout the state, but are generally located in forested areas and served by rural cooperatives
MONTANA | RELIABILITY MAP
TOTAL CUSTOMER INTERRUPTIONS PER COVERED CUSTOMER BY COUNTY
(MT, 2018-2022)
INTERRUPTIONS/CUSTOMER
INSIGHTS
Counties experiencing the greatest number of customer interruptions per capita are spread throughout the state
This is unlike other states in WECC where reliability is geographically
correlated
Could be due to rural, high volume of radial overhead infrastructure and dese vegetation from protected lands
High winds generally drive outages across the least reliable sections of the Montana grid
Wind was identified as the primary driver of customer interruptions in all
counties with below average reliability except Lincoln County where it was the second leading driver (see slide 24)
Reliability issues are generally concentrated among rural electric cooperatives
Counties with the highest volume of interruptions per customer are generally served by rural electric cooperatives, while IOUs serve the most reliable portions of the state
Hill County Electric Cooperative
0
19
38
INSUFFICIENT COVERAGE
Northern Lights/Flathead/Lincoln Electric Cooperatives
Vigilante Electric Cooperative
Mid-Yellowstone/Tongue
River Electric Cooperative
Fergus Electric Cooperative

## Slide 22: Extreme outages are generally attributable to higher wind speeds, but a high coincidence of outages with low wind speeds indicates vegetation contact could be a key driver
28 30 32 34 36 38 40 42 44 46 48 50 52 54 56 58 60 62 64 66 68 70 72 74 76 78 80 82 84 86
MAX WIND GUST SPEED (mph)
5
0
100
95
90
85
80
75
70
65
60
55
50
45
40
35
30
25
20
15
MONTANA | HAZARD 1—WINDSTORM
CUMULATIVE OUTAGE OCCURRENCE(%)
GUST SPEED & POWER OUTAGES
0-0.5 Customer Outage Ratio
>0.5 Cutomer Outage Ratio
Designing, building, inspecting, and maintaining (i.e. veg management) assets for below 40 mph wind gusts will not address 50% of more severe and costly outages, which occur at higher wind speeds.
UNDERSTANDING THE DATA
Extreme outages (>50% of customers out) are more likely to be coincident with >40 mph wind speeds than non-extreme outages
About 50% of extreme outages are attributable to wind speeds above 40 mph, compared to just 30% of non-extreme outages
The gap between the curves indicates that extreme outages are generally more likely to be coincident with higher wind speeds than non-extreme outages
ASSET PLANNING INSIGHTS
Prioritizing vegetation management and active inspection could address a significant portion of wind-driven outages
Almost 80% of extreme outages and 90% of non-extreme outages occur at wind speeds < 50 mph, which are more likely attributable to vegetation contact or aging equipment rather than direct failure
Designing to 67 mph wind speeds would historically address most extreme outages, including those caused by direct failure
Low-Cost: Pole Reinforcement (Trussing, Guy Cables, Concrete Base, etc.), Pole Material Upgrades, Decreased Spans, Vegetation Management
High-Cost: Undergrounding

## Slide 23
Despite the importance of wind and wildfire in the West, utilities could bolster their capital alignment with historical & future risk by conducting asset-level vulnerability assessments
EXECUTIVE SUMMARY | FINAL INVESTMENT CONSIDERATIONS
ASSET | INVESTMENT | COST | HAZARDS
POLES & STRUCTURES | Pole Reinforcement | M | 3
 | Pole Upgrades | M | 3
 | Dead-End Structures | M | 2
 | Decreased Span | M | 2
 | Pole Wrapping | L | 1
CONDUCTORS | Undergrounding | H | 4
 | Reconductoring | M | 4
 | Covered Conductors | M | 4
 | Hardening/Rebuilds | L | 1
SUBSTATIONS | Substation Elevation | H | 1
 | Control House Remediation | H | 1
 | Enclosures | H | 3
 | Reclosers/Switchgear | M | 2
 | Flood Walls | M | 1
 | Cooling Mechanisms | M | 1
PLANNING TOOLS | Vegetation Management | H | 3
 | Dynamic Line Rating (DLR) | L | 1
Wildfire Planning Tools |  | M | 1
High Cost Moderate Cost Low Cost
Invest against windstorms: Windstorms are the most widespread and severe cause of extreme outages across WECC in the past 5 years. While utilities are investing some capital against wind risk, the universal elevated exposure requires an increased volume of capital towards mitigations. Given its homogenous exposure, wind upgrades could be pursued as updates to design standards rather than targeted, ad hoc investments like substation upgrades.
Continue existing wildfire mitigations: While wildfire exposure of the past 5 years varies by geography, the cost of ignition remains inordinately high in comparison to other hazards. Therefore, even though ignition probability may be low, the high expected cost, coupled with the expected increase in exposure due to changes in climate, substantiates increased investment in mitigation.
Utilities can better justify expensive investments like undergrounding by ensuring upgrades are done on feeders that are exposed to multiple hazards, having a double dividend effect on the investment.
Quantify extreme weather risk in dollars: In order to optimally allocate capital expenditures to buy down the most extreme weather risk for the least amount of dollars, utilities must quantify the cost and benefits of the risk and subsequent investment. The utilities that are most effectively optimizing their plans are implementing asset-level vulnerability assessments, using down downscaled climate projections to predict impacts out to mid-century. Baringa will be expanding on how to conduct such analysis in phase 4 of this project.
STATE OF THE GRID REPORT | FINAL INVESTMENT CONSIDERATIONS

## Slide 24: 4. Question & Answer
24 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential
Open Discussion

## Slide 25: If you would like to learn more about the GRACI technical assistance program, please reach out DEQ or Baringa for access to the reports
QUESTION & ANSWER | OPEN DISCUSSION
GRID RESILIENCE REPORT (GRR)
25 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential
STATE OF THE GRID REPORT (SOGR)
NEXT STEPS
Open up presentation to Question & Answer
Please reach out to MT Utilities or Baringa for:
  Access to these reports
  Additional follow up technical assistance opportunities
Prepare for the next round of 40101(d) solicitations

## Slide 26: Appendix
26 | Copyright © Baringa Partners LLP 2025. All rights reserved. This document is subject to contract and contains confidential and proprietary information.
Baringa Confidential

## Slide 27: Historically, severe outages in Montana have primarily been driven by wind-related events, making this a priority for additional investment
EXECUTIVE SUMMARY | PROJECT AND DELIVERABLE OVERVIEW
A severe outage is defined as one in which >50% of customers in a county are out simultaneously, or at least 30,0000 customers in a county experience an outage simultaneously, whichever is less
Sources: Found in slide notes
PROGRAM OBJECTIVE
Help state energy offices and select utilities assess how to use 40101(d) funding to best strengthen the power grid against extreme weather, by:
Assessing the unique needs of each state energy office
Analyzing future exposure to extreme weather in the state, its coincidence with energy assets, and potential impacts
Attributing outages to weather events and commenting on the
alignment of utility capital spending with historical exposure
Outlining a benefit-cost methodology to improve asset planning
KEY FINDINGS
Hazard Analysis:
High wind speeds are the key driver of severe outages* on the Montana grid
High wind speeds are coincident with 60% of all customer interruptions from severe outages during 2018-22
Only 2% of interruptions from severe outages were not coincident with extreme weather, justifying expanded weatherization and resilience-related investments
Capital Planning Insights:
IOU-1 is investing heavily to mitigate wildfire risk, but could consider whether investments addressing wind should be expanded
Purely wind-driven outages account for 40% of customer
interruptions from severe outages in IOU-1’s service territory
IOU-1 is generally spending effectively given its relatively low spend per line mile and SAIDI minutes compared to other utilities in WECC
DELIVERABLE OBJECTIVE
This deliverable seeks to:
Attribute historical outages in the state to specific weather events and comment on which events are driving the most customer interruptions in the state
Analyze a select utility’s capital plan and assess the alignment between their resilience spending and the weather events driving outages in their service territory

## Slide 28: Stakeholders can use this report to inform funding allocation and capital planning, and should engage with GRACI phase 4 to learn best practices for investment valuation and prioritization
EXECUTIVE SUMMARY | NEXT STEPS
ENGAGE WITH GRACI PHASE 4
Summary: Phase 4 of the GRACI project will
include a webinar and report outlining Baringa’s prioritization and valuation methodology for utility capital investments.
WEBINAR DETAILS
Date: June 30, 2025
Time: 3:00-4:30 PM EST
Location: Zoom Meeting
Baringa will present its prioritization and valuation methodology during NASEO’s standing Grid Resilience Grant Implementation Cohort Meeting.
RECOMMENDED PREPARATION
No preparation is required, but coming with questions or background about how your state or utility currently approaches benefit-cost analysis for grid investments could make for a more engaging conversation.
EVALUATE ALIGNMENT WITH
PHASE 3 FINDINGS
Summary: States and utilities could evaluate whether their funding allocation or capital spending aligns with the key hazards identified in this report.
KEY QUESTIONS FOR SEOs
Are the key hazards identified in this report already a state priority?
Has a significant portion of resilience funding been allocated to addressing these hazards?
Is grant funding flowing to areas of the grid that experience a high volume of interruptions per customer?
KEY QUESTIONS FOR UTILITIES
Is it worth increasing spend to increase reliability given our position on the spend metrics chart? (See Slide 37)
Should we increase spend addressing the hazards listed in “Future Investment Opportunities?” (See Slide 39)
CONSIDER ADDITIONAL TECHNICAL ASSISTANCE NEEDS
Summary: Consider additional technical assistance needs to inform future 40101(d) funding allocation or capital planning.
TIMELINE OF EXISTING ENGAGEMENT
Technical assistance under the current engagement is slated to end July 1, 2025.
NEXT STEPS
Confirm whether the needs below remain the priority for your office or new focus areas have arisen. Our team will communicate these needs to the DOE for evaluation and inquiry for potential funding.
MT PRIORITIES
Small utility asset-level vulnerability studies
Utility application administration assistance
State Energy Security Plan support
FERC-1920 analysis
Analysis on North Plains Connector

## Slide 29: Baringa will aid 11 states in Western Electric Coordinating Council (WECC) in assessing how to allocate funding to address extreme weather risk
SCOPE & BACKGROUND | OVERVIEW
Western Electricity Coordinating Council
Region of Study
WECC
Geography: 11 states
Total Population: 76.5 million
Project Purpose: Help Grid Resilience State & Tribal Formula Grant recipients assess how to use their grants to best strengthen the power grid against extreme weather and natural disasters, while providing community benefits
Data Usage: As part of the project, Baringa will develop a report that summarizes downscale climate forecasts, general asset vulnerability, and adaptation investments. The goal with this deliverable is to assess state-wide exposure to future extreme weather and indicate high risk assets and mitigation strategies. Data will be investigated for statistical relationships as well as mapped to state geographies for visual analysis.
Outputs: 11 Grid Resilience Risk Reports (1/state) detailing changes in hazards, notable patterns and risk areas, and impacts to energy infrastructure.
Analysis Sponsorship Partners
11 State Energy
Offices
11 Utilities*
SMEs, Advisors
Our Understanding
Purpose & Stakeholders

## Slide 30: There are four main phases that will help to aid SEOs and utilities in assessing allocating resilience funds
SCOPE & BACKGROUND | APPROACH
CURRENT & FUTURE STATE OF THE GRID REPORT
Deliverable: Report outlining historic utility reliability performance and assess current resilience strategies
Objective: Establish a relationship between historic weather and outages and the effectiveness of utility investments to mitigate risk
Deliverable: Document explaining benefit-cost methodology for assessing tradeoff options among investment options
Objective: Equip SEOs and utilities with prioritization framework to assess resilience investments
GRID RESILIENCE RISK, VULNERABILITIES AND INVESTMENT REPORT
Deliverable: Report summarizing downscale climate forecasts, general asset vulnerability, and adaptation investments
Objective: Assess state-wide exposure to future extreme weather and indicate high risk assets and mitigation strategies
KICKOFF STATE ENERGY OFFICE
SUMMARIES
Deliverable: Reports detailing state resilience needs, concerns, and existing practices
Objective: Improve understanding of state resilience needs, agree on proposed project plan, and align on 11 utilities for Current & Future State of the Grid Report
PRIORITIZATION & VALUATION METHODOLOGY
Grid Resilience Technical Assistance Consortium
(GRACI)
PHASE 1.0
PHASE 2.0
PHASE 4.0
PHASE 3.0
UTILITY BENEFIT

## Slide 31: GRACI WORKPLAN
TODAY
Jul
Aug
Sep
Oct
Nov
Dec Jan 25’
Feb Mar
Apr
May
Jun
Jul
Aug
M4. Draft State of the Grid Report
M6. Draft
Prioritization Report
SOTG Report utility working sessions
M5. Final Report
M7. Webinar
& Final Report
Kickoff(s)
M8. Closeout
Project Management & Monthly Status Reports
1. KICKOFF & STATE ENERGY OFFICE SUMMARIES
3. CURRENT & FUTURE STATE OF THE GRID REPORT
M2. Grid Resilience Reports (2 states)
M3. Grid Resilience Reports
Webinar
Failure Modes & Adaptations Workshop(s)
Calculate climate forecasts including flood, wind, rain, heat, cold, ice, wildfire, drought for 3 scenarios
Define failure modes and thresholds by asset class and hazard Build inventory of investment options to mitigate vulnerabilities
2. GRID RESILIENCE RISKS, VULNERABILITIES, AND INVESTMENT REPORT
4. PRIORITIZATION & VALUATION METHODOLOGY REPORT
M1. SEO Summary & Project plan
Confirm kick-off content with DOE
Host kick-off meeting(s) with State Energy Offices
DOE presentation of State’s priorities, selection of 11 focus utilities,
approved project plan
Analyze current grid performance from regional MED outage and reliability data
Assess utilities’ existing investment strategies,
performance, and regulatory alignment
Integrate failure modes with asset condition and comment on expected evolution
Detail method to forecast financial impact for two sample asset locations Host webinar sharing results of C&FS Grid Report
Define a benefit-cost methodology for assessing investment tradeoffs Provide ways to quantify community benefits and integrate into BCA Develop resilience plan prioritization framework for State Energy Offices Provide example BCAs
Host webinar sharing results of Report
Transfer completed deliverables to DOE and complete project closeout
SCOPE & BACKGROUND | WORKPLAN
Key meeting/ workshop Milestone #. Deliverable
availability.
Timing is highly dependent on availability of State Energy Offices, selected utilities, and timely DOE review. Schedule is subject to change based on

## Slide 32: The State of the Grid Report will provide recommendations and insights into most effective resilience projects, highest risk locations, and strategies for improving capital spend efficiency
GRACI | PHASE 3
1 STATE OF THE GRID REPORT | BENEFITS
2 STATE OF THE GRID REPORT | BENEFITS
Improved understanding of how extreme weather impacts outage and ignition rates in your service territory
DELIVERABLE | EXTREME WEATHER ANALYSIS
Analyze 5 years of publicly available extreme weather and outage data to determine which type of events cause the largest outages and ignitions.
Comment on expected change in outages and ignitions as a function of climate projections.
Actionable insights to improve capital effectiveness
that addresses extreme weather risk
DELIVERABLE | INVESTMENT PLAN REVIEW
Review most recent investment plan to determine effectiveness of normalized capital spend in mitigating outages and ignitions from extreme weather.
Results will be anonymously compared with other participants to help outline resilience best practices and most effective mitigations.
Baringa is conscious of data privacy and sensitivities and is more than willing to work with your team to address concerns.