## Slide 1: Flathead Electric Microgrid Projects
Essex
Cooke City
Whitefish

## Slide 2: Project Drivers
New Technology
New Solution to Existing Problems
Value Stacking
Outage Mitigation

## Slide 3: Feeder Details
Essex Feeder
  30 Mile Radial Feeder
  387 Total Meters
    Average Load = 475 kW
  176 Meters in Community of Essex at end of feeder
    Average Load = 218 kW

## Slide 4: Essex Feeder

## Slide 5: Outage Details
Looked at 10 Year Outage History
  310 Total Outages on Feeder
    Most of any feeder
  160 Outages with fault upstream of the last recloser
  Determined how much battery was needed

## Slide 6: Battery Size
Size Battery to ride through MOST outages
Chart: Outage Mitigation by Battery Size
| 1 MWH | 2 MWH | 3 MWH
Number of Outages Eliminated | 0.63125 | 0.93125 | 0.9625
Outage Minutes Eliminated | 0.38 | 0.62 | 0.7

## Slide 7: FEC Perspective
Location – Not In My Backyard
  Thank you to MDT
Size Matters
  Vendors focus on larger scale projects
Approach
  Turnkey from vendor

## Slide 8: Cooke City Feeder

## Slide 9: Whitefish Community Solar
Community Solar Project
BESS & Solar

## Slide 10: Project Funding Options
Essex
  Grid Resilience - 40101(C)
  NRECA Consortium (application submitted)
Cooke City
  Energy Improvements in Rural and Remote Areas
  NRECA Consortium
Whitefish
  Undecided- 40101(D)?

## Slide 11: Lookout Ridge
Solar – 150 kW
Battery – 375 kW
Natural Gas Gen – 150 kW
Independent Power Systems

## Slide 12: Lookout Ridge
  LOR Outage Example
  Utility (FEC)
  Load
  Inverter

## Slide 13: Lookout Ridge
Hourly Inverter Statistics