## DEQ-7 trigger value
DRAFT
Appendix O (Surface Water Trigger Value Spreadsheet)
TRIGGER VALUE CALCULATION FOR ADJACENT TO SURFACE WATER DILUTION ANALYSIS
An analysis of the effect of the proposed absorption system on the quality of any adjacent surface water
is required by ARM 17.36.124 and 17.30.715(1)(g). The increase in the nutrient concentration in the surface water
cannot exceed the trigger value (0.01 mg/L nitrate and 0.001 mg/L phosphorus as set forth in department circular DEQ-7).
NITROGEN DILUTION EQUATION: (n)(QD)((CD)(1-Nredn) + (QL)(CL) - (CL) = Cf
(n)(QD) + QL
Variables defined below
NITRATE CALCULATION:
n = | 25 |  | Number of absorption systems
QD = | 26.7 | ft³/d | Effluent flow rate from each absorption system (or, or if (n) is equal to 1.0 the combined flow rate from all sources) (1)
CD = | 14.6 | mg/L | Nitrate concentration discharged from wastewater system (2) . For situations where the wastewater systems have different effluent concentrations impacting the surface water, a flow weighted concentration should be calculated using the worksheet in the "Flow Weighted Concentration" tab (3).
Nredn | 0.3 |  | Nitrate Attenuation factor per ARM 17.30.517(1)(d)(vii) [For example, a value of 0.3 means 30% of the nitrogen is attenuated from the load discharged from the absorption system]
QL = | 0.3 | ft³/s | Surface water flow rate (seasonal 14Q5)
CL = | 0 | mg/L | Nitrate concentration in surface water; can typically assume zero because the concentration increase, not total concentration, is required for trigger value.
Cf = | 0.25658 | mg/L | Nitrate concentration increase in surface water. Must be less than 0.01 mg/L (DEQ-7) to be considered a nonsignificant nitrate increase
PHOSPHORUS DILUTION EQUATION: (n)(QD)(CD) + (QL)(CL) - (CL) = Cf
(n)(QD) + QL
Variables defined below
PHOSPHORUS CALCULATION:
n = | 3 |  | Number of absorption systems
QD = | 26.7 | ft³/d | Effluent flow rate from each absorption system (or, or if (n) is equal to 1.0 the combined flow rate from all sources) (1)
CD = | 10.6 | mg/L | Phosphorus concentration discharged from wastewater system (10.6 mg/L for residential strength wastewater)
QL = | 0.3 | ft³/s | Surface water flow rate (seasonal 14Q5)
CL = | 0 | mg/L | Phosphorus concentration in surface water; can typically assume zero since the concentration increase, not total concentration, is required for trigger value.
Cf = | 0.032656 | mg/L | Phosphorus concentration increase in surface water, must be less than 0.001 mg/L (DEQ-7) to be considered nonsignificant phosphorus increase
NOTES:
(1) | Effluent rate for a 2 - 5 bedroom single living unit is 200 gpd (26.7 ft3/d).
(2) | 50 mg/L for conventional wastewater system; 24 mg/L for level 2.
(3) | Different nitrate effluent concentrations may be due to use of level 2 systems, or maybe due to nitrate attenuation pursuant to ARM 17.30.517(1)(d)(vi)
Blue shaded cells indicate parameters to be entered by the user.
Red shaded cells are formulas that should not be changed by the user

## Flow Weighted Concentration
CALCULATION SHEET FOR FLOW-WEIGHTED CONCENTRATION VALUE (CD) IN SURFACE WATER TRIGGER VALUE SPREADSHEET
WASTEWATER SYSTEM ID | NONDEGRADATION EFFLUENT RATE (ft3/d) | EFFLUENT CONCENTRATION IMPACTING SURFACE WATER (mg/L) (1) | CALCULATED LOAD (ft3/d) x (mg/L) | NOTES
Lot A | 200 | 24 | 4800 | EXAMPLE ONLY
Lot B | 500 | 18.6 | 9300 | EXAMPLE ONLY
Lot C | 200 | 42 | 8400 | EXAMPLE ONLY
Lot D | 400 | 50 | 20000 | EXAMPLE ONLY
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
N/A | 1300 | N/A | 42500
FLOW WEIGHTED CONCENTRATION ("CD" in Trigger Value Spreadsheet) |  |  | 32.6923