## Calculator
Liquid Chlorination Metering Pump Setup: |  |  |  |  | Enter Values in Yellow Boxes
System Design Perameters:
Start with entering the flow rate of your water source (well pump) the chlorine will be injected into, and the maximum Gallon per Hour (GPH) rating of your injection pump. Next enter the final desired concentration of chlorine in your source water, this can be adusted as desired.
| Flow Rate of System Well Pump (gpm) |  |  | 14 | gpm
| Injection Pump Max GPH rating (on pump) |  |  | 0.42 | GPH
| Desired Clorine Dose Concentration (ppm) |  |  | 1 | ppm
Metering Pump Settings:
To determine the stroke (and speed) settings for your injection pump, enter the starting chlorine concentration of the disinfectant you will be using (bleach = 6%, Sodiun Hypochlorite =12%) and adjust the Final Diluted Batch Concentration until the stroke setting (metering pump with stroke control only) is between 50-100%. A green OK will appear on the right when in range. On metering pumps that also has speed adjustment, the stroke can be further adjusted so that both the stroke and speed are between 50-100%.
| Starting Chlorine Concentration (CL %) |  |  | 12 | %
| Final Diluted Batch Concentration (CL %) |  |  | 0.27 | %
Mertering Pump with Stoke Length Control Only Setting:
| Chlorine Batch Chemical feed Rate (GPH ) |  |  | 0.31111
| Pump Maximum GPH rating (on pump) |  |  | 0.42
| Stroke Setting on pump (%) |  |  | 0.74074 | OK
Metering Pump with Stroke length and Speed Control Setting and Adjustment:
| Chlorine Batch Chemical feed Rate (GPH ) |  |  | 0.31111
| Pump Maximum GPH rating (on pump) |  |  | 0.42
| Stroke Setting on pump (%) |  |  | 0.9 | OK
| Speed Setting on pump (%) |  |  | 0.82305 | OK
Batch Tank Solution Mixing:
Create the size and concentration of the chorine batch solution to be injected by the injection pump. Adjust the Starting gallons of CL concentrate until a usable size of Batch Solution is created,
| Starting gallons of Chlorine Concentrate |  |  | 0.27 | gal
| Amount of water to add (per batch) |  |  | 11.73 | gal
| Total Size of Batch Solution |  |  | 12 | gal
Storage Tank Dosing/Disinfection Calculator:
Using Sodium Hypochlorite or Bleach:
| Tank Volume (gallons) | Desired Concentration (ppm) | Added Cl Conc. (%) | Amount of Cl to Add |  |  | Volume Conversions
1 teaspoon = 1/6 oz (0.167 oz)
| 2500 | 1 | 12% | 0.020833 | (gal) |  | 1 Tablespoon = 1/2 oz (0.5 oz)
|  |  |  | 2.6667 | (oz) |  | 1/4 cup = 2 oz
1 cup = 8 oz
Gallons (gal) to Fluid Ounces (oz) Converter | [6 empty] | 1 pint = 16 oz
| 0.27 | equals (=) | 34.56 |  |  |  | 1 quart = 32 oz
| gallons (gal) |  | Ounces (oz) |  |  |  | 1 gallon = 128 oz
Chemical Feed Rate:
| Flow (gpm) |  | Dose (ppm)
| 14 | X | 1 | x 60 min/hr | = | 0.31111 | Chemical feed rate (gph)
0.27
Batch Solution Strength (%)
Batch Volume and Size Calculations
| CL |  |  |  |  | final (gal)
| Higher (Start %) |  |  |  | ratio | CL (from above)
|  | 12 | Desired Conc | 0.27 | 0.0225 | 0.27
0.27
|  | 0 |  | 11.73 | 0.9775 | 11.73 | I feel this is correct
| Lower (Start %) |  |  | 12 |  | water (calculated)
Water